INSTALLATION INSTRUCTIONS – IAC NOISE-LOCK DOORS

INSTALLATION PROCEDURE

PREPARATION:  Clear all debris and foreign matter from around the wall opening and floor.  Prior to uncrating, check rough opening size for height, width, square and wall thickness.  If not in accordance with this specification, do not begin.  Contact IAC at 718-931-8000 for instructions.

Door is designed to be installed on top of a hard, smooth finished surface.

PRE-HUNG ASSEMBLY:  Each leaf and frame is factory fitted and match marked to insure proper alignment, seal and operation.  Do not mix and match assemblies.

UNCRATING:  Carefully open crate and/or box.  Check Swing.  If correct, remove banding.  Open leaf approximately 120°.  Lift off hinge and set aside.  Remove plug buttons and temporary fasteners and “separate” frame sections (see isometric). Remove spreader bar.  The assembly is now in 3 pieces: leaf, male frame and female frame.

SETTING FRAME:  If required, first install the sill plate with the smooth side up.  Plumb and align female section hinge side in opening in accordance with tolerances shown.  Fasten with one fastener at each hinge, careful not to dimple frame.  Do not install male side at this time.

Carefully mount leaf and close.  Check seal and shim frame if required to obtain a complete seal at head and jambs.  You have now simulated the factory pre-hung position.  Mark accordingly.  Carefully remove door leaf.  Fasten latch side of frame using one fastener at top and bottom opposite hinge location.

Carefully mount leaf to verify correct continuous seal.  Again remove leaf.  Notch male section corresponding to previously installed fasteners (Total of 4 plcs).   Pack frame with insulation and position male frame section into place. Secure frame with remaining fasteners being careful not to dimple frame.

FINAL ADJUSTMENT:  Mount leaf, open and close to insure proper seal.  If ok, mount any additional hardware.  Adjust bottom seal by opening leaf and loosening the 2 screws on door edge allowing seal to drop down.  Open and close door 2 or 3 times.  Open and tighten two screws.  If operation is satisfactory, replace plug button and caulk exterior joints where frame meets wall.

Demonstrate and instruct the owner on operation and maintenance.